## Analog
Pembina Pipeline Corp.
Analog & Tank(T) Points List generated at 2023/01/30 09:35
Remote Information
| Analog Name | Analog Description | EGU Min | EGU Max | Units | In? | Address | Out? | Address | Display | Group
H_SK - H_SK-Horizon Skaro Station (APSI Address 48 (x30) on connection MQ_H_SK)
| H_SK_KHR | H_SK PLC Hour | 0 | 23 | h | yes | 40100 unsign 16 int | yes | 42403 unsign 16 int | H_SK | Horizon
| H_SK_KMN | H_SK PLC Minute | 0 | 59 | m | yes | 40101 unsign 16 int | yes | 42404 unsign 16 int | H_SK | Horizon
| H_SK_KSC | H_SK PLC Second | 0 | 59 | s | yes | 40102 unsign 16 int | yes | 42405 unsign 16 int | H_SK | Horizon
| H_SK_KDY | H_SK PLC Day | 1 | 31 |  | yes | 40103 unsign 16 int | yes | 42401 unsign 16 int | H_SK | Horizon
| H_SK_KMH | H_SK PLC Month | 1 | 12 |  | yes | 40104 unsign 16 int | yes | 42400 unsign 16 int | H_SK | Horizon
| H_SK_KYR | H_SK PLC Year | 2015 | 2100 |  | yes | 40105 unsign 16 int | yes | 42402 unsign 16 int | H_SK | Horizon
| H_SK_DAY | H_SK PLC Day of the Week | 0 | 7 | # | yes | 40106 unsign 16 int | yes | 42406 unsign 16 int | H_SK | Horizon
| H_SK_TOS | H_SK Time Of Snapshot | 0 | 1440 | min | yes | 40107 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT001S | H_SK Station Mainline Pump Suction Pressure Sna | 0 | 7000 | kPa | yes | 40108 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT011S | H_SK Station Mainline Pump Discharge Pressure S | 0 | 7000 | kPa | yes | 40109 unsign 16 int | no |  | H_SK | Horizon
| H_SK_FT061A | H_SK Station Mainline Flow 1 | 0 | 3300 | m3/h | yes | 40110 unsign 16 int | no |  | H_SK | Horizon
| H_SK_FT061B | H_SK Station Mainline Flow 2 | 0 | 3300 | m3/h | yes | 40111 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT001 | H_SK Station Inlet Pressure 1 | 0 | 10000 | kPa | yes | 40112 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT002 | H_SK Station Inlet Pressure 2 | 0 | 7000 | kPa | yes | 40113 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT011 | H_SK Station Outlet Pressure Control | 0 | 10000 | kPa | yes | 40114 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT012 | H_SK Station Outlet Pressure | 0 | 10000 | kPa | yes | 40115 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT013 | H_SK Station Outlet Pressure OPP Shutdown | 0 | 10000 | kPa | yes | 40116 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT111 | H_SK Pump-001 Suction Pressure | 0 | 10000 | kPa | yes | 40117 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT112 | H_SK Pump-001 Discharge Pressure | 0 | 10000 | kPa | yes | 40118 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT121 | H_SK Pump-002 Suction Pressure | 0 | 10000 | kPa | yes | 40119 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT122 | H_SK Pump-002 Discharge Pressure | 0 | 10000 | kPa | yes | 40120 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT131 | H_SK Pump-003 Suction Pressure | 0 | 10000 | kPa | yes | 40121 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT132 | H_SK Pump-003 Discharge Pressure | 0 | 10000 | kPa | yes | 40122 unsign 16 int | no |  | H_SK | Horizon
| H_SK_TT001 | H_SK Station Inlet Temperature | -20 | 50 | C | yes | 40127 unsign 16 int | no |  | H_SK | Horizon
| H_SK_TT011 | H_SK Station Outlet Temperature | -50 | 100 | C | yes | 40128 unsign 16 int | no |  | H_SK | Horizon
| H_SK_LIT720 | H_SK Sump Tank Level | 0 | 100 | % | yes | 40129 unsign 16 int | no |  | H_SK | Horizon
| H_SK_VFD001SPD | H_SK VFD-001 Speed Feedback | 0 | 100 | % | yes | 40130 unsign 16 int | no |  | H_SK | Horizon
| H_SK_VFD002SPD | H_SK VFD-002 Speed Feedback | 0 | 100 | % | yes | 40131 unsign 16 int | no |  | H_SK | Horizon
| H_SK_VFD003SPD | H_SK VFD-003 Speed Feedback | 0 | 100 | % | yes | 40132 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PIDS_SP | H_SK Station Suction Pressure Setpoint | 0 | 10000 | kPa | yes | 40134 unsign 16 int | yes | 42447 unsign 16 int | H_SK | Horizon
| H_SK_PIDD_SP | H_SK Station Discharge Pressure Setpoint | 0 | 10000 | kPa | yes | 40135 unsign 16 int | yes | 42448 unsign 16 int | H_SK | Horizon
| H_SK_PID_OPM | H_SK Station PID Controller Manual Output | 0 | 100 | % | yes | 40136 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PID_OP | H_SK Station PID Controller Output Speed | 0 | 100 | % | yes | 40137 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PIMAOP | H_SK Maximum Allowable Operating Discharge Pres | 0 | 10000 | kPa | yes | 40138 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PDT001 | H_SK Strainer Differential Pressure | 0 | 10000 | kPaD | yes | 40139 unsign 16 int | no |  | H_SK | Horizon
| H_SK_PT015 | H_SK Station Outlet Mainline Pressure | 0 | 10000 | kPa | yes | 40140 unsign 16 int | no |  | H_SK | Horizon
| H_SK_JT101 | H_SK Cathodic Rectifier Amperage | 0 | 75 | A | yes | 40142 unsign 16 int | no |  | H_SK | Horizon
| H_SK_ET101 | H_SK Cathodic Rectifier Voltage | 0 | 75 | V | yes | 40143 unsign 16 int | no |  | H_SK | Horizon
| H_SK_HZFLOW | H_SK Horizon Flow (from Host) | 0 | 3300 | m3/h | yes | 40144 unsign 16 int | yes | 42449 unsign 16 int | H_SK | Horizon
| H_SK_MB001_VAB | H_SK MB001 Line Voltage AB | 0 | 50 | V | yes | 40145 unsign 16 int | no |  | H_SK | Horizon
| H_SK_MB001_VBC | H_SK MB001 Line Voltage BC | 0 | 50 | V | yes | 40146 unsign 16 int | no |  | H_SK | Horizon
| H_SK_MB001_VCA | H_SK MB001 Line Voltage CA | 0 | 50 | V | yes | 40147 unsign 16 int | no |  | H_SK | Horizon
| H_SK_TT011S | H_SK Station Discharge Temperature Snapshot | -50 | 100 | C | yes | 40148 unsign 16 int | no |  | H_SK | Horizon
| H_SK_HZDT | H_HT Horizon Station Density | 0 | 1000 | kg/m3 | yes | 40149 unsign 16 int | yes | 42450 unsign 16 int | H_SK | Development
| H_SK_TT905 | H_SK Electrical Room Temperature | 0 | 100 | C | yes | 40150 unsign 16 int | no |  | H_SK | Horizon
| H_SK_TT906 | H_SK Control Room Temperature2 | 0 | 100 | C | yes | 40151 unsign 16 int | no |  | H_SK | Horizon

## Rate
Pembina Pipeline Corp.
Rate Points List generated at 2023/01/30 09:35
Remote Information
| Rate Name | Rate Description | EGU Min | EGU Max | Units | Type | Pulse Address | Analog Address | Display | Group
H_SK - H_SK-Horizon Skaro Station (APSI Address 48 (x30) on connection MQ_H_SK)
(No rate points defined)

## Status
Pembina Pipeline Corp.
Status/Digital Points List generated at 2023/01/30 09:35
Remote Information
| Status Name | Status Description | In? | Width | Bit 1 Address | Bit 2 Address | Out? | Open/On/Start | Close/Off/Stop | Display | AlmTxt | Group
H_SK - H_SK-Horizon Skaro Station (APSI Address 48 (x30) on connection MQ_H_SK)
| H_SK_TAH906 | H_SK TT906 Temperature High | yes | 1 | 40084/12 |  | no |  |  | H_SK | HITEMP | Horizon
| H_SK_TAL906 | H_SK TT906 Temperature Low | yes | 1 | 40084/13 |  | no |  |  | H_SK | LOTEMP | Horizon
| H_SK_TAH905 | H_SK TT905 Temperature High | yes | 1 | 40084/14 |  | no |  |  | H_SK | HITEMP | Horizon
| H_SK_TAL905 | H_SK TT905 Temperature Low | yes | 1 | 40084/15 |  | no |  |  | H_SK | LOTEMP | Horizon
| H_SK_PDAH001 | H_SK Suction Strainer Differential Press. High | yes | 1 | 40085/04 |  | no |  |  | H_SK | HIDIFF | Horizon
| H_SK_DPR_MISMATCH | H_SK DPR Mismatch between Station PLC and OPP | yes | 1 | 40085/05 |  | no |  |  | H_SK | PLC/A | Horizon
| H_SK_PAHH013 | H_SK Station Outlet OPP Disc Pres Hi Hi | yes | 1 | 40085/06 |  | no |  |  | H_SK | HHPRS | Horizon
| H_SK_STN_SUCT_PAH | H_SK Station Inlet Pressure Hi Alarm | yes | 1 | 40085/07 |  | no |  |  | H_SK | HISUCT | Horizon
| H_SK_STN_SUCT_PAL | H_SK Station Inlet Pressure Lo Alarm | yes | 1 | 40085/08 |  | no |  |  | H_SK | LOSUCT | Horizon
| H_SK_STN_SUCT_PALL | H_SK Station Inlet Pressure Lo Lo Alarm | yes | 1 | 40085/09 |  | no |  |  | H_SK | LLSUCT | Horizon
| H_SK_STN_DISC_PAHH | H_SK Station Outlet Pressure Hi Hi Alarm | yes | 1 | 40085/10 |  | no |  |  | H_SK | HHDISC | Horizon
| H_SK_LAH | H_SK Sump Tank Level High Common Alarm | yes | 1 | 40085/11 |  | no |  |  | H_SK | HISUMP | Horizon
| H_SK_STN_DISC_PAH | H_SK Station Outlet Pressure High Alarm | yes | 1 | 40085/14 |  | no |  |  | H_SK | HIDISC | Horizon
| H_SK_STN_DISC_PALL | H_SK Station Outlet Pressure Low Low Alarm | yes | 1 | 40085/15 |  | no |  |  | H_SK | LLDISC | Horizon
| H_SK_P003 | H_SK Pump-003 Status | yes | 1 | 40087/00 |  | yes | 1074 | 1075 | H_SK | ###### | Horizon
| H_SK_P003_AV | H_SK Pump-003 Available To Run | yes | 1 | 40087/01 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_P003_EFL | H_SK Pump-003 Electrical Fault Lockout | yes | 1 | 40087/02 |  | no |  |  | H_SK | E/LOCK | Horizon
| H_SK_P003_EFR | H_SK Pump-003 Electrical Fault Resettable | yes | 1 | 40087/03 |  | no |  |  | H_SK | ERESET | Horizon
| H_SK_P003_MFL | H_SK Pump-003 Mechanical Fault Lockout | yes | 1 | 40087/05 |  | no |  |  | H_SK | M/LOCK | Horizon
| H_SK_P003_MFR | H_SK Pump-003 Mechanical Fault Resetable | yes | 1 | 40087/06 |  | no |  |  | H_SK | MRESET | Horizon
| H_SK_P001 | H_SK Pump-001 Status | yes | 1 | 40088/00 |  | yes | 1070 | 1071 | H_SK | ###### | Horizon
| H_SK_P001_AV | H_SK Pump-001 Available To Run | yes | 1 | 40088/01 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_P001_EFL | H_SK Pump-001 Electrical Fault Lockout | yes | 1 | 40088/02 |  | no |  |  | H_SK | E/LOCK | Horizon
| H_SK_P001_EFR | H_SK Pump-001 Electrical Fault Resettable | yes | 1 | 40088/03 |  | no |  |  | H_SK | ERESET | Horizon
| H_SK_P001_MFL | H_SK Pump-001 Mechanical Fault Lockout | yes | 1 | 40088/05 |  | no |  |  | H_SK | M/LOCK | Horizon
| H_SK_P001_MFR | H_SK Pump-001 Mechanical Fault Resetable | yes | 1 | 40088/06 |  | no |  |  | H_SK | M/RSET | Horizon
| H_SK_P002 | H_SK Pump-002 Status | yes | 1 | 40088/08 |  | yes | 1072 | 1073 | H_SK | ###### | Horizon
| H_SK_P002_AV | H_SK Pump-002 Available To Run | yes | 1 | 40088/09 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_P002_EFL | H_SK Pump-002 Electrical Fault Lockout | yes | 1 | 40088/10 |  | no |  |  | H_SK | E/LOCK | Horizon
| H_SK_P002_EFR | H_SK Pump-002 Electrical Fault Resettable | yes | 1 | 40088/11 |  | no |  |  | H_SK | ERESET | Horizon
| H_SK_P002_MFL | H_SK Pump-002 Mechanical Fault Lockout | yes | 1 | 40088/13 |  | no |  |  | H_SK | M/LOCK | Horizon
| H_SK_P002_MFR | H_SK Pump-002 Mechanical Fault Resetable | yes | 1 | 40088/14 |  | no |  |  | H_SK | M/RSET | Horizon
| H_SK_VFD003M | H_SK VFD-003 Mode | yes | 1 | 40089/00 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_VFD003 | H_SK VFD-003 Running Status | yes | 1 | 40089/01 |  | no |  |  | H_SK | VFD | Horizon
| H_SK_VFD003FL | H_SK VFD-003 Drive Fault | yes | 1 | 40089/03 |  | no |  |  | H_SK | VFD/FL | Horizon
| H_SK_VFD003R | H_SK VFD-003 Ready | yes | 1 | 40089/04 |  | no |  |  | H_SK | READY | Horizon
| H_SK_VFD003FB004 | H_SK VFD-003 Input Breaker Status | yes | 1 | 40089/05 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_VFD00386 | H_SK VFD-003 Breaker Relay 86 Tripped | yes | 1 | 40089/06 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_VFD003SPDF | H_SK VFD-003 Motor Speed Fail | yes | 1 | 40089/07 |  | no |  |  | H_SK | SPD/F | Horizon
| H_SK_VFD001M | H_SK VFD-001 Mode | yes | 1 | 40090/00 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_VFD001 | H_SK VFD-001 Running Status | yes | 1 | 40090/01 |  | no |  |  | H_SK | VFD | Horizon
| H_SK_VFD001FL | H_SK VFD-001 Drive Fault | yes | 1 | 40090/03 |  | no |  |  | H_SK | VFD/FL | Horizon
| H_SK_VFD001R | H_SK VFD-001 Ready | yes | 1 | 40090/04 |  | no |  |  | H_SK | READY | Horizon
| H_SK_VFD001FB002 | H_SK VFD-001 Input Breaker Status | yes | 1 | 40090/05 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_VFD00186 | H_SK VFD-001 Breaker Relay 86 Tripped | yes | 1 | 40090/06 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_VFD001SPDF | H_SK VFD-001 Motor Speed Fail | yes | 1 | 40090/07 |  | no |  |  | H_SK | SPD/F | Horizon
| H_SK_VFD002M | H_SK VFD-002 Mode | yes | 1 | 40090/08 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_VFD002 | H_SK VFD-002 Running Status | yes | 1 | 40090/09 |  | no |  |  | H_SK | VFD | Horizon
| H_SK_VFD002FL | H_SK VFD-002 Drive Fault | yes | 1 | 40090/11 |  | no |  |  | H_SK | VFD/FL | Horizon
| H_SK_VFD002R | H_SK VFD-002 Ready | yes | 1 | 40090/12 |  | no |  |  | H_SK | READY | Horizon
| H_SK_VFD002FB003 | H_SK VFD-002 Input Breaker Status | yes | 1 | 40090/13 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_VFD00286 | H_SK VFD-002 Breaker Relay 86 Tripped | yes | 1 | 40090/14 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_VFD002SPDF | H_SK VFD-002 Motor Speed Fail | yes | 1 | 40090/15 |  | no |  |  | H_SK | SPD/F | Horizon
| H_SK_ESDV001 | H_SK Mainline Pump Inlet ESD Valve | yes | 2 | 40091/00 | 40091/01 | yes | 1036 | 1037 | H_SK | ###### | Horizon
| H_SK_ESDV012 | H_SK Mainline Pump Outlet Bypass ESD Valve | yes | 2 | 40091/02 | 40091/03 | yes | 1038 | 1039 | H_SK | ###### | Horizon
| H_SK_ESDV002 | H_SK Mainline Pump Inlet Bypass ESD Valve | yes | 2 | 40091/04 | 40091/05 | yes | 1040 | 1041 | H_SK | ###### | Horizon
| H_SK_ESDV011 | H_SK Mainline Pump Outlet ESD Valve | yes | 2 | 40091/06 | 40091/07 | yes | 1042 | 1043 | H_SK | ###### | Horizon
| H_SK_MLV119S | H_SK Mainline Station Suction Valve | yes | 2 | 40091/08 | 40091/09 | yes | 1044 | 1045 | H_SK | ###### | Horizon
| H_SK_MLV119D | H_SK Mainline Station Discharge Valve | yes | 2 | 40091/10 | 40091/11 | yes | 1046 | 1047 | H_SK | ###### | Horizon
| H_SK_MLV119S_ARM | H_SK Mainline Station Suction Valve Armed | yes | 1 | 40091/12 |  | yes | 1050 |  | H_SK | ###### | Horizon
| H_SK_MLV119D_ARM | H_SK Mainline Station Discharge Valve Armed | yes | 1 | 40091/14 |  | yes | 1052 |  | H_SK | ###### | Horizon
| H_SK_UV111 | H_SK Pump-001 Suction Valve | yes | 2 | 40092/00 | 40092/01 | yes | 1020 | 1021 | H_SK | ###### | Horizon
| H_SK_UV112 | H_SK Pump-001 Discharge Valve | yes | 2 | 40092/02 | 40092/03 | yes | 1022 | 1023 | H_SK | ###### | Horizon
| H_SK_UV121 | H_SK Pump-002 Suction Valve | yes | 2 | 40092/04 | 40092/05 | yes | 1024 | 1025 | H_SK | ###### | Horizon
| H_SK_UV122 | H_SK Pump-002 Discharge Valve | yes | 2 | 40092/06 | 40092/07 | yes | 1026 | 1027 | H_SK | ###### | Horizon
| H_SK_UV131 | H_SK Pump-003 Suction Valve | yes | 2 | 40092/08 | 40092/09 | yes | 1028 | 1029 | H_SK | ###### | Horizon
| H_SK_UV132 | H_SK Pump-003 Discharge Valve | yes | 2 | 40092/10 | 40092/11 | yes | 1030 | 1031 | H_SK | ###### | Horizon
| H_SK_UV111_F | H_SK Pump-001 Suction Valve Fail | yes | 1 | 40093/00 |  | no |  |  | H_SK | F | Horizon
| H_SK_UV112_F | H_SK Pump-001 Discharge Valve Fail | yes | 1 | 40093/01 |  | no |  |  | H_SK | F | Horizon
| H_SK_UV121_F | H_SK Pump-002 Suction Valve Fail | yes | 1 | 40093/02 |  | no |  |  | H_SK | F | Horizon
| H_SK_UV122_F | H_SK Pump-002 Discharge Valve Fail | yes | 1 | 40093/03 |  | no |  |  | H_SK | F | Horizon
| H_SK_UV131_F | H_SK Pump-003 Suction Valve Fail | yes | 1 | 40093/04 |  | no |  |  | H_SK | F | Horizon
| H_SK_UV132_F | H_SK Pump-003 Discharge Valve Fail | yes | 1 | 40093/05 |  | no |  |  | H_SK | F | Horizon
| H_SK_ESDV001_F | H_SK Mainline Pump Inlet ESD Valve Fail | yes | 1 | 40093/08 |  | no |  |  | H_SK | F | Horizon
| H_SK_ESDV012_F | H_SK Mainline Pump Outlet Bypass ESD Valve Fail | yes | 1 | 40093/09 |  | no |  |  | H_SK | F | Horizon
| H_SK_ESDV002_F | H_SK Mainline Pump Inlet Bypass ESD Valve Fail | yes | 1 | 40093/10 |  | no |  |  | H_SK | F | Horizon
| H_SK_ESDV011_F | H_SK Mainline Pump Outlet ESD Valve Fail | yes | 1 | 40093/11 |  | no |  |  | H_SK | F | Horizon
| H_SK_MLV119S_F | H_SK Mainline Station Suction Valve Fail | yes | 1 | 40093/12 |  | no |  |  | H_SK | F | Horizon
| H_SK_MLV119D_F | H_SK Mainline Station Discharge Valve Fail | yes | 1 | 40093/13 |  | no |  |  | H_SK | F | Horizon
| H_SK_UV111_HS | H_SK Pump-001 Suction Valve Mode | yes | 1 | 40094/00 |  | no |  |  | H_SK | H | Horizon
| H_SK_UV112_HS | H_SK Pump-001 Discharge Valve Mode | yes | 1 | 40094/01 |  | no |  |  | H_SK | H | Horizon
| H_SK_UV121_HS | H_SK Pump-002 Suction Valve Mode | yes | 1 | 40094/02 |  | no |  |  | H_SK | H | Horizon
| H_SK_UV122_HS | H_SK Pump-002 Discharge Valve Mode | yes | 1 | 40094/03 |  | no |  |  | H_SK | H | Horizon
| H_SK_UV131_HS | H_SK Pump-003 Suction Valve Mode | yes | 1 | 40094/04 |  | no |  |  | H_SK | H | Horizon
| H_SK_UV132_HS | H_SK Pump-003 Discharge Valve Mode | yes | 1 | 40094/05 |  | no |  |  | H_SK | H | Horizon
| H_SK_ESDV001_HS | H_SK Mainline Pump Inlet ESDV Valve Mode | yes | 1 | 40094/08 |  | no |  |  | H_SK | H | Horizon
| H_SK_ESDV012_HS | H_SK Mainline Pump Outlet Bypass ESDV Mode | yes | 1 | 40094/09 |  | no |  |  | H_SK | H | Horizon
| H_SK_ESDV002_HS | H_SK Mainline Pump Inlet Bypass ESDV Mode | yes | 1 | 40094/10 |  | no |  |  | H_SK | H | Horizon
| H_SK_ESDV011_HS | H_SK Mainline Pump Outlet ESDV Mode | yes | 1 | 40094/11 |  | no |  |  | H_SK | H | Horizon
| H_SK_MLV119S_HS | H_SK Mainline Station Suction Valve Mode | yes | 1 | 40094/12 |  | no |  |  | H_SK | H | Horizon
| H_SK_MLV119D_HS | H_SK Mainline Station Discharge Valve Mode | yes | 1 | 40094/13 |  | no |  |  | H_SK | H | Horizon
| H_SK_ZI001 | H_SK Inlet Pig Signal | yes | 1 | 40095/00 |  | no |  |  | H_SK | SCRPR | Horizon
| H_SK_ZI002 | H_SK Intermediate Pig Signal | yes | 1 | 40095/01 |  | no |  |  | H_SK | SCRPR | Horizon
| H_SK_ZI011 | H_SK Outlet Pig signal | yes | 1 | 40095/02 |  | no |  |  | H_SK | SCRPR | Horizon
| H_SK_PIG_BYP_F | H_SK Stn Pig Bypass Sequence Fail | yes | 1 | 40095/03 |  | no |  |  | H_SK | SCRP/F | Horizon
| H_SK_P011 | H_SK Sump Pump P-011 Run Status | yes | 1 | 40095/04 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_LSHH_PMP_FLR | H_SK Pump Building Floor Drain HiHi(Call-Out) | yes | 1 | 40095/05 |  | no |  |  | H_SK | HHSUMP | Horizon
| H_SK_LSHH_PMP_FLR_FM | H_SK Pump Bldg Floor Drain HiHi(Call-Out)(FM) | yes | 1 | 40095/05 |  | no |  |  | H_SK | X | FOREMAN
| H_SK_PIG_BYP | H_SK Stn Pig Sequence Bypass | yes | 1 | 40095/06 |  | no |  |  | H_SK | BYPASS | Horizon
| H_SK_LAHH | H_SK Sump Tank Level High High Common Alarm | yes | 1 | 40095/10 |  | no |  |  | H_SK | HHSUMP | Horizon
| H_SK_LAHH_FM | H_SK Sump Tank Level Switch High High Alarm FM | yes | 1 | 40095/10 |  | no |  |  | H_SK | X | FOREMAN
| H_SK_24V_F | H_SK Common 24 VDC Power Failure | yes | 1 | 40096/00 |  | no |  |  | H_SK | 24V/FL | Horizon
| H_SK_4160V_F | H_SK Common 4160 VAC Power Failure | yes | 1 | 40096/02 |  | no |  |  | H_SK | 4160/F | Horizon
| H_SK_PIDM | H_SK PID Controller Auto/Manual | yes | 1 | 40096/03 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_MB5KV52 | H_SK SWGR-001 5kV Main Breaker MB001 | yes | 1 | 40096/04 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_MB5KVLR | H_SK SWGR-001 5kV Main Breaker MB001 Mode | yes | 1 | 40096/05 |  | no |  |  | H_SK | H | Horizon
| H_SK_MB5KVF | H_SK SWGR-001 5kV Main Breaker MB001 Fail to Tr | yes | 1 | 40096/06 |  | no |  |  | H_SK | BKR/A | Horizon
| H_SK_TR5KV52 | H_SK TR-001 5KV Breaker FB001 Status | yes | 1 | 40096/07 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_TR5KVLR | H_SK TR-001 5KV Breaker FB001 Mode | yes | 1 | 40096/08 |  | no |  |  | H_SK | H | Horizon
| H_SK_TR5KVF | H_SK TR-001 5KV Breaker FB001 Fail to Trip | yes | 1 | 40096/09 |  | no |  |  | H_SK | BKR/A | Horizon
| H_SK_MCC001_MB | H_SK MCC-001 480 VAC Breaker Status | yes | 1 | 40096/10 |  | no |  |  | H_SK | BKR/OP | Horizon
| H_SK_MCC001_MB_FTT | H_SK MCC-001 480 VAC Breaker Fail to Trip | yes | 1 | 40096/11 |  | no |  |  | H_SK | BKR/A | Horizon
| H_SK_VFD001_ST_INH | H_SK VFD-001 Pump-001 Start Inhibit | yes | 1 | 40096/12 |  | no |  |  | H_SK | TIME/O | Horizon
| H_SK_VFD002_ST_INH | H_SK VFD-002 Pump-002 Start Inhibit | yes | 1 | 40096/13 |  | no |  |  | H_SK | TIME/O | Horizon
| H_SK_VFD003_ST_INH | H_SK VFD-003 Pump-003 Start Inhibit | yes | 1 | 40096/14 |  | no |  |  | H_SK | TIME/O | Horizon
| H_SK_MODEM | H_SK SCADA DBU Data | yes | 1 | 40097/00 |  | yes | 1008 | 1009 | H_SK | ###### | Horizon_comms
| H_SK_BTMODEM1 | H_SK Programming Modem Power Enabled | yes | 1 | 40097/01 |  | yes | 1011 | 1012 | H_SK | MODEM | Horizon
| H_SK_TREQ | H_SK Time Update Requested | yes | 1 | 40097/02 |  | no |  |  | H_SK | TIMERQ | Horizon
| H_SK_HEARTBEAT | H_SK Communication Heart Beat | yes | 1 | 40097/03 |  | yes | 1006 | 1006 | H_SK | ###### | Horizon
| H_SK_UPS_F | H_SK Station Common UPS Fault | yes | 1 | 40097/04 |  | no |  |  | H_SK | UPS/FL | Horizon
| H_SK_UPS_ALM | H_SK Station Common UPS Alarm | yes | 1 | 40097/05 |  | no |  |  | H_SK | UPS/A | Horizon
| H_SK_HCPL001_FLT | H_SK BU-001 HVAC HCPL-001 Common Fail | yes | 1 | 40097/07 |  | no |  |  | H_SK | HVAC/F | Horizon
| H_SK_INTRUSION | H_SK Common Building Intrusion Alarm | yes | 1 | 40097/09 |  | no |  |  | H_SK | INTRDR | Horizon
| H_SK_BU001_TAHH | H_SK BU-001 Common Temperature High High | yes | 1 | 40097/10 |  | no |  |  | H_SK | HHTEMP | Horizon
| H_SK_COMMF | H_SK General Station COM Fail | yes | 1 | 40097/14 |  | no |  |  | H_SK | COM/FL | Horizon
| H_SK_UPS_LOW | H_SK Station Common UPS Low | yes | 1 | 40097/15 |  | no |  |  | H_SK | UPS/LO | Horizon
| H_SK_AAHHLEL | H_SK LEL High High Level Detected on Site | yes | 1 | 40098/01 |  | no |  |  | H_SK | HH LEL | Horizon
| H_SK_AAHHLEL_FM | H_SK LEL High High Level Detected on Site (FM) | yes | 1 | 40098/01 |  | no |  |  | H_SK | X | FOREMAN
| H_SK_AAHHH2S | H_SK H2S High High Level Detected on Site | yes | 1 | 40098/03 |  | no |  |  | H_SK | HH H2S | Horizon
| H_SK_AAHHH2S_FM | H_SK H2S High High Level Detected on Site (FM) | yes | 1 | 40098/03 |  | no |  |  | H_SK | X | FOREMAN
| H_SK_AAFIRE | H_SK Fire Detected On Site | yes | 1 | 40098/04 |  | no |  |  | H_SK | FIRE | Horizon
| H_SK_AAFIRE_FM | H_SK Fire Detected On Site (FM) | yes | 1 | 40098/04 |  | no |  |  | H_SK | X | FOREMAN
| H_SK_AALEL_F | H_SK LEL System Fault | yes | 1 | 40098/05 |  | no |  |  | H_SK | LEL/FL | Horizon
| H_SK_AAH2S_F | H_SK H2S System Fault | yes | 1 | 40098/06 |  | no |  |  | H_SK | H2S/FL | Horizon
| H_SK_AAFIRE_F | H_SK Fire Detection System Fault | yes | 1 | 40098/07 |  | no |  |  | H_SK | FIRE/F | Horizon
| H_SK_STN_VIBRATION_TEST_2 | H_SK Secondary Station In Vibration Test Permis | yes | 1 | 40098/14 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_STN_VIBRATION_TEST | H_SK Station In Vibration Test Mode | yes | 1 | 40098/15 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_ESD | H_SK STA ESD | yes | 1 | 40099/00 |  | yes | 1000 | 1000 | H_SK | ###### | Horizon
| H_SK_ESD_FM | H_SK STA ESD (FM) | yes | 1 | 40099/00 |  | no |  |  | H_SK | X | FOREMAN
| H_SK_RESET | H_SK Station Alarm Reset | yes | 1 | 40099/01 |  | yes | 1001 | 1001 | H_SK | ###### | Horizon
| H_SK_ATTEND | H_SK Site Attend Mode | yes | 1 | 40099/02 |  | no |  |  | H_SK | ATTEND | Horizon
| H_SK_AUTOSD | H_SK Station Auto Shutdown | yes | 1 | 40099/03 |  | yes | 1003 | 1003 | H_SK | ###### | Horizon
| H_SK_STA_MODE | H_SK Station Mode | yes | 1 | 40099/04 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_STA_FLOWPATH | H_SK Pipeline Flow Path Permissive | yes | 1 | 40099/06 |  | no |  |  | H_SK | ###### | Horizon
| H_SK_XESBSUMP | H_SK Station Sump ESD Bypass | yes | 1 | 40099/08 |  | no |  |  | H_SK | BYPASS | Horizon
| H_SK_FGBYP | H_SK Fire and Gas Detector Bypass | yes | 1 | 40099/09 |  | no |  |  | H_SK | FG/BP | Horizon
| H_SK_PLCAV | H_SK Hot Standby Backup PLC Not Available | yes | 1 | 40099/10 |  | no |  |  | H_SK | PLC/NA | Horizon
| H_SK_PLC_F | H_SK PLC Failure | yes | 1 | 40099/11 |  | no |  |  | H_SK | PLC/F | Horizon
| H_SK_CALIBRM | H_SK Transmitter in Calibration Bypass | yes | 1 | 40099/12 |  | no |  |  | H_SK | CALIBR | Horizon
| H_SK_ANLG_F | H_SK Station Transmitter Common Fail Alarm | yes | 1 | 40099/13 |  | no |  |  | H_SK | TX/FL | Horizon
| H_SK_SCADA_COM_F | H_SK SCADA Comm Fail | yes | 1 | 40099/14 |  | no |  |  | H_SK | # COMM | Horizon
| H_SK_OPP_PLC_F | H_SK OPP PLC Fail | yes | 1 | 40099/15 |  | no |  |  | H_SK | OPP/F | Horizon